## Cover
Commissioning Document Package
Project | Packaging Line 3
Customer | Sample Customer
Machine / Line | Infeed conveyor + hydraulic press
PLC / Controller | S7-1516F / TIA Portal V19
Document No. | CP-0001
Revision | 0
Date | 2026-10-08
Prepared by | CommissionPack demo
Source IO list | tia_plc_tags_sample.xlsx
Contents
DI Checkout | 20 IO points
DO Checkout | 9 IO points
AI Loop Check | 4 IO points
AO Loop Check | 2 IO points
FAT Protocol
SAT Protocol
Punch List
Sign-off
Summary
Safety-related IO points (marked red) | 4
This package is a working document. The responsible engineer must check it against the approved drawings, the functional description and the safety validation plan.
CommissionPack 0.1.0 - 2026-10-08 12:53

## Summary
Summary - Packaging Line 3
Customer: Sample Customer ¦ Machine / Line: Infeed conveyor + hydraulic press ¦ Document No.: CP-0001 ¦ Revision: 0
Section | Total | OK | NOK | N/A | Open | Complete
Digital input checkout
Digital output checkout
Analog input loop check
Analog output loop check
Total
Analog sheets count test points (5 per channel).
Open A (Punch List)

## DI Checkout
DI Checkout - Packaging Line 3
Customer: Sample Customer ¦ Machine / Line: Infeed conveyor + hydraulic press ¦ Document No.: CP-0001 ¦ Revision: 0
No. | Tag | Address | Comment | Location | Device type | Test instruction | Expected result | Status | Tested by | Date | Remarks
1 | EStop_Panel_CH1 | %I0.0 | Emergency stop main panel channel 1 |  | Safety device | Operate the safety device (e.g. press E-stop, open door). Check the input goes to 0 (NC). Reset the device. Check the input goes back to 1. Test both channels if 2-channel. | Correct address. Input LED, PLC and HMI show the same state.
2 | EStop_Panel_CH2 | %I0.1 | Emergency stop main panel channel 2 |  | Safety device | Operate the safety device (e.g. press E-stop, open door). Check the input goes to 0 (NC). Reset the device. Check the input goes back to 1. Test both channels if 2-channel. | Correct address. Input LED, PLC and HMI show the same state.
3 | Door1_Closed | %I0.2 | Safety door 1 closed (interlock) |  | Safety device | Operate the safety device (e.g. press E-stop, open door). Check the input goes to 0 (NC). Reset the device. Check the input goes back to 1. Test both channels if 2-channel. | Correct address. Input LED, PLC and HMI show the same state.
4 | LightCurtain_OK | %I0.3 | Light curtain infeed OK |  | Safety device | Operate the safety device (e.g. press E-stop, open door). Check the input goes to 0 (NC). Reset the device. Check the input goes back to 1. Test both channels if 2-channel. | Correct address. Input LED, PLC and HMI show the same state.
5 | PB_Start | %I0.4 | Push button start |  | Push button / Selector | Press / switch the operator device. Check the input changes 0 -> 1. Release. Check 1 -> 0. | Correct address. Input LED, PLC and HMI show the same state.
6 | PB_Stop | %I0.5 | Push button stop |  | Push button / Selector | Press / switch the operator device. Check the input changes 0 -> 1. Release. Check 1 -> 0. | Correct address. Input LED, PLC and HMI show the same state.
7 | PB_Reset | %I0.6 | Fault reset |  | Push button / Selector | Press / switch the operator device. Check the input changes 0 -> 1. Release. Check 1 -> 0. | Correct address. Input LED, PLC and HMI show the same state.
8 | SS_AutoManual | %I0.7 | Selector auto / manual |  | Push button / Selector | Press / switch the operator device. Check the input changes 0 -> 1. Release. Check 1 -> 0. | Correct address. Input LED, PLC and HMI show the same state.
9 | Q1_MCB_OK | %I1.0 | Main breaker Q1 feedback |  | Breaker / Feedback | Switch the breaker / contactor ON and OFF. Check the feedback input follows the device state. | Correct address. Input LED, PLC and HMI show the same state.
10 | M1_Conveyor_Running | %I1.1 | Conveyor motor M1 running feedback |  | Motor / Contactor | Run the motor in manual mode (area safe). Check the running / feedback input = 1. Stop. Check = 0. | Correct address. Input LED, PLC and HMI show the same state.
11 | M2_Pump_Running | %I1.2 | Hydraulic pump M2 running |  | Motor / Contactor | Run the motor in manual mode (area safe). Check the running / feedback input = 1. Stop. Check = 0. | Correct address. Input LED, PLC and HMI show the same state.
12 | Cyl1_Extended | %I1.3 | Cylinder 1 end position extended |  | Valve / Cylinder | Move the cylinder / valve to the end position. Check the end-position input = 1. Move back. Check = 0. | Correct address. Input LED, PLC and HMI show the same state.
13 | Cyl1_Retracted | %I1.4 | Cylinder 1 end position retracted |  | Valve / Cylinder | Move the cylinder / valve to the end position. Check the end-position input = 1. Move back. Check = 0. | Correct address. Input LED, PLC and HMI show the same state.
14 | Prox_PartPresent | %I1.5 | Inductive sensor part present |  | Sensor / Switch | Activate the sensor with the real target. Check the sensor LED and input = 1. Remove the target. Check input = 0. | Correct address. Input LED, PLC and HMI show the same state.
15 | Photo_Infeed | %I1.6 | Photo sensor infeed |  | Sensor / Switch | Activate the sensor with the real target. Check the sensor LED and input = 1. Remove the target. Check input = 0. | Correct address. Input LED, PLC and HMI show the same state.
16 | Photo_Outfeed | %I1.7 | Photo sensor outfeed |  | Sensor / Switch | Activate the sensor with the real target. Check the sensor LED and input = 1. Remove the target. Check input = 0. | Correct address. Input LED, PLC and HMI show the same state.
17 | LS_Tank_High | %I2.0 | Level switch tank high |  | Level | Simulate the switch point (test button, test pressure or real level). Check the input changes at the set value and the HMI shows the state. | Correct address. Input LED, PLC and HMI show the same state.
18 | PS_Air_OK | %I2.1 | Pressure switch compressed air OK |  | Pressure | Simulate the switch point (test button, test pressure or real level). Check the input changes at the set value and the HMI shows the state. | Correct address. Input LED, PLC and HMI show the same state.
19 | VFD1_Ready | %I2.2 | G120 drive conveyor ready |  | Drive / VFD | Change the drive state (ready / fault / running). Check the status input follows the drive display. | Correct address. Input LED, PLC and HMI show the same state.
20 | VFD1_Fault | %I2.3 | G120 drive conveyor fault |  | Drive / VFD | Change the drive state (ready / fault / running). Check the status input follows the drive display. | Correct address. Input LED, PLC and HMI show the same state.

## DO Checkout
DO Checkout - Packaging Line 3
Customer: Sample Customer ¦ Machine / Line: Infeed conveyor + hydraulic press ¦ Document No.: CP-0001 ¦ Revision: 0
No. | Tag | Address | Comment | Location | Device type | Test instruction | Expected result | Status | Tested by | Date | Remarks
1 | M1_Contactor | %Q0.0 | Conveyor motor M1 contactor |  | Motor / Contactor | Make sure the motor can run safely. Set the output in the watch table. Check the contactor pulls in and the rotation direction. Reset the output. | Correct device reacts. No other output or device changes.
2 | M2_Pump_Contactor | %Q0.1 | Hydraulic pump M2 contactor |  | Motor / Contactor | Make sure the motor can run safely. Set the output in the watch table. Check the contactor pulls in and the rotation direction. Reset the output. | Correct device reacts. No other output or device changes.
3 | YV1_Cyl1_Extend | %Q0.2 | Valve cylinder 1 extend |  | Valve / Cylinder | Make sure the actuator area is clear. Set the output. Check the coil LED and the actuator moves. Reset the output. | Correct device reacts. No other output or device changes.
4 | YV2_Cyl1_Retract | %Q0.3 | Valve cylinder 1 retract |  | Valve / Cylinder | Make sure the actuator area is clear. Set the output. Check the coil LED and the actuator moves. Reset the output. | Correct device reacts. No other output or device changes.
5 | HL_Green | %Q0.4 | Signal lamp green |  | Lamp / Horn | Set the output. Check the lamp / horn works. Reset the output. | Correct device reacts. No other output or device changes.
6 | HL_Red | %Q0.5 | Signal lamp red |  | Lamp / Horn | Set the output. Check the lamp / horn works. Reset the output. | Correct device reacts. No other output or device changes.
7 | Horn | %Q0.6 | Alarm horn |  | Lamp / Horn | Set the output. Check the lamp / horn works. Reset the output. | Correct device reacts. No other output or device changes.
8 | Heater1 | %Q0.7 | Heater zone 1 contactor |  | Heater | Set the output for a short time only. Check the heater contactor pulls in. Reset the output. | Correct device reacts. No other output or device changes.
9 | VFD1_Enable | %Q1.0 | G120 drive conveyor enable |  | Drive / VFD | Set the command output (enable / start). Check the drive receives the command (drive status display). Reset. | Correct device reacts. No other output or device changes.

## AI Loop Check
AI Loop Check - Packaging Line 3
Customer: Sample Customer ¦ Machine / Line: Infeed conveyor + hydraulic press ¦ Document No.: CP-0001 ¦ Revision: 0
Method: inject the signal with a calibrator at the terminal. Read the value in the PLC/HMI. Enter the measured value. Status is calculated automatically.
No. | Tag | Address | Comment | Signal | Range min | Range max | Unit | Test point | Expected signal | Raw value (S7) | Expected value | Measured value | Deviation % of span | Tolerance % | Status | Tested by | Date | Remarks
1 | TT101_Temp | %IW64 | Temperature tank PT100 | 4-20 mA | 0 | 100 |  | 0% | [5 empty] | 0.5
| TT101_Temp | %IW64 | [5 empty] | 25%
| TT101_Temp | %IW64 | [5 empty] | 50%
| TT101_Temp | %IW64 | [5 empty] | 75%
| TT101_Temp | %IW64 | [5 empty] | 100%
2 | PT102_Pressure | %IW66 | Hydraulic pressure transmitter | 4-20 mA | 0 | 100 |  | 0% | [5 empty] | 0.5
| PT102_Pressure | %IW66 | [5 empty] | 25%
| PT102_Pressure | %IW66 | [5 empty] | 50%
| PT102_Pressure | %IW66 | [5 empty] | 75%
| PT102_Pressure | %IW66 | [5 empty] | 100%
3 | LT103_Level | %IW68 | Tank level transmitter | 4-20 mA | 0 | 100 |  | 0% | [5 empty] | 0.5
| LT103_Level | %IW68 | [5 empty] | 25%
| LT103_Level | %IW68 | [5 empty] | 50%
| LT103_Level | %IW68 | [5 empty] | 75%
| LT103_Level | %IW68 | [5 empty] | 100%
4 | FT104_Flow | %IW70 | Cooling water flow | 4-20 mA | 0 | 100 |  | 0% | [5 empty] | 0.5
| FT104_Flow | %IW70 | [5 empty] | 25%
| FT104_Flow | %IW70 | [5 empty] | 50%
| FT104_Flow | %IW70 | [5 empty] | 75%
| FT104_Flow | %IW70 | [5 empty] | 100%

## AO Loop Check
AO Loop Check - Packaging Line 3
Customer: Sample Customer ¦ Machine / Line: Infeed conveyor + hydraulic press ¦ Document No.: CP-0001 ¦ Revision: 0
Method: set the value in the PLC watch table. Measure the signal at the terminal. Convert it to engineering units and enter it. Status is calculated automatically.
No. | Tag | Address | Comment | Signal | Range min | Range max | Unit | Test point | Expected signal | Raw value (S7) | Expected value | Measured value | Deviation % of span | Tolerance % | Status | Tested by | Date | Remarks
1 | VFD1_SpeedSP | %QW80 | Conveyor speed setpoint to drive | 4-20 mA | 0 | 100 |  | 0% | [5 empty] | 0.5
| VFD1_SpeedSP | %QW80 | [5 empty] | 25%
| VFD1_SpeedSP | %QW80 | [5 empty] | 50%
| VFD1_SpeedSP | %QW80 | [5 empty] | 75%
| VFD1_SpeedSP | %QW80 | [5 empty] | 100%
2 | PV201_Position | %QW82 | Proportional valve position setpoint | 4-20 mA | 0 | 100 |  | 0% | [5 empty] | 0.5
| PV201_Position | %QW82 | [5 empty] | 25%
| PV201_Position | %QW82 | [5 empty] | 50%
| PV201_Position | %QW82 | [5 empty] | 75%
| PV201_Position | %QW82 | [5 empty] | 100%

## FAT Protocol
FAT Protocol - Packaging Line 3
Customer: Sample Customer ¦ Machine / Line: Infeed conveyor + hydraulic press ¦ Document No.: CP-0001 ¦ Revision: 0
No. | Section | Check item | Acceptance criterion | Status | Remarks | Tested by | Date
1 | Documentation | Electrical drawings are the current revision and match the panel. | No difference found, or differences recorded in the punch list.
2 | Documentation | IO list matches the drawings and the PLC tag table. | 100 % match.
3 | Documentation | PLC / HMI / drive software versions are recorded (name, version, date). | Versions written in the remarks.
4 | Panel inspection | Labels, wire markers and terminal numbers match the drawings. | Visual check OK.
5 | Panel inspection | PE connections are complete and tight. | Continuity test done, values recorded.
6 | Panel inspection | Fuse, MCB and overload settings match the drawings. | All values checked.
7 | Power-up | Insulation and continuity tests are done before power-up. | Test report attached.
8 | Power-up | Supply voltages (AC and 24 VDC) are within tolerance. | Measured values recorded.
9 | Power-up | PLC, IO modules and HMI start without errors. | Diagnostic buffer has no active errors.
10 | Communication | All network devices are online. Device names and IP addresses match the network list. | No device fault in the PLC.
11 | Communication | Disconnect one network device. Check the communication alarm. | Alarm appears with the correct text. Machine goes to a safe state.
12 | IO tests | Digital input checkout (20 IO points) | 100 % OK, see sheet 'DI Checkout'.
13 | IO tests | Digital output checkout (9 IO points) | 100 % OK, see sheet 'DO Checkout'.
14 | IO tests | Analog input loop check (4 IO points) | 100 % OK, see sheet 'AI Loop Check'.
15 | IO tests | Analog output loop check (2 IO points) | 100 % OK, see sheet 'AO Loop Check'.
16 | Functions | Each actuator works in manual mode. | All manual functions OK.
17 | Functions | The automatic sequence runs according to the functional description. | Each step tested.
18 | Functions | Interlocks and permissives work as specified. | Each interlock tested.
19 | Alarms and HMI | Each alarm appears with the correct text and class. Acknowledge and reset work. | Alarm list checked.
20 | Alarms and HMI | HMI screens, navigation and user levels are as specified. | All screens checked.
21 | Safety | Each safety function is tested according to the safety validation plan. | Validation report signed. |  | Safety-related IO points (marked red): 4
22 | Safety | Emergency stop stops all hazardous motion. Restart needs a manual reset. | Tested at each E-stop device.
23 | Safety | Safety program signature / checksum is recorded. | Value written in the remarks.
24 | Drives | Drive parameters are saved. Motor data and speed scaling are correct. | Parameter backup available.
25 | Closure | Backups of PLC, HMI and drive projects are handed over. | Backup file names recorded.
26 | Closure | The FAT punch list is issued and agreed. | No open A-items.

## SAT Protocol
SAT Protocol - Packaging Line 3
Customer: Sample Customer ¦ Machine / Line: Infeed conveyor + hydraulic press ¦ Document No.: CP-0001 ¦ Revision: 0
No. | Section | Check item | Acceptance criterion | Status | Remarks | Tested by | Date
1 | Installation | Equipment is installed at the final location according to the layout. | Visual check OK.
2 | Installation | Field cables are installed, marked and terminated according to the cable list. | Cable list checked.
3 | Installation | Earthing and equipotential bonding are complete. | Measured values recorded.
4 | Pre-commissioning | Insulation tests of field cables are done. | Test report attached.
5 | Pre-commissioning | FAT punch items are closed or transferred to the SAT punch list. | No open FAT A-items.
6 | Pre-commissioning | The software version on site is the approved FAT version (or changes are documented). | Version recorded.
7 | IO tests | Digital input checkout (20 IO points) | 100 % OK, see sheet 'DI Checkout'.
8 | IO tests | Digital output checkout (9 IO points) | 100 % OK, see sheet 'DO Checkout'.
9 | IO tests | Analog input loop check (4 IO points) | 100 % OK, see sheet 'AI Loop Check'.
10 | IO tests | Analog output loop check (2 IO points) | 100 % OK, see sheet 'AO Loop Check'.
11 | Field devices | Sensor positions and switching points are adjusted on the real process. | All sensors checked.
12 | Field devices | Motor rotation directions are correct on site. | All motors checked.
13 | Field devices | Instruments are calibrated. Certificates are available. | Certificates attached.
14 | Process functions | The automatic run works with real product / material. | Run without critical fault.
15 | Process functions | Interfaces to other machines and site systems are tested (signals, PROFINET, OPC UA). | Interface list checked.
16 | Safety | Safety functions are validated on site. Guards, doors and light curtains are tested in the final position. | Validation report signed.
17 | Performance | Capacity / cycle time test: target and measured values. | Measured >= target.
18 | Performance | Continuous run test (agreed duration, e.g. 24 h / 72 h). | No critical fault during the test.
19 | Handover | Operator and maintenance training is done. | Attendance list signed.
20 | Handover | As-built drawings, manuals and software backups are handed over. | Handover list signed.

## Punch List
Punch List - Packaging Line 3
Customer: Sample Customer ¦ Machine / Line: Infeed conveyor + hydraulic press ¦ Document No.: CP-0001 ¦ Revision: 0
No. | Reference | Description | Location | Responsible | Category (A/B/C) | Due date | Remarks | Status | Closed on
A = must be closed before acceptance. B = close before handover. C = improvement, no effect on acceptance.
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60

## Sign-off
Sign-off - Packaging Line 3
Customer: Sample Customer ¦ Machine / Line: Infeed conveyor + hydraulic press ¦ Document No.: CP-0001 ¦ Revision: 0
FAT Protocol
Acceptance decision: | [ ] Accepted [ ] Accepted with punch items (A-items = 0) [ ] Not accepted
Role | Company | Name | Signature | Date
Supplier / Integrator
Customer representative
Third party (optional)
SAT Protocol
Acceptance decision: | [ ] Accepted [ ] Accepted with punch items (A-items = 0) [ ] Not accepted
Role | Company | Name | Signature | Date
Supplier / Integrator
Customer representative
Third party (optional)